## 1
欧洲化学哈萨克斯坦化工综合体项目
DOC.NO: | [13 empty] | Rev.D01
No. | Issue Date | Sec & Page | Content | Initiator | Vendor Reply(1) |  |  |  | Vendor's Proposal(2) |  | Ans.Date | TCC Comments on Vendor's Proposal | Vendor's Reply to TCC Comments | Remarks / Status
[5 empty] | A | B | C | D | Sec & Page | Content
1 |  |  | 如果是单台电机， 则交接点位于电机接线盒处。从变电所到电机的动力电缆属于甲方设计及供货范围。 For motor, the interface is located at the motor junction box. The design and supply of power cables from the substation to the motor is in buyer’s scope. 对于成套电控柜（电伴热箱等），则交接点位于成套电控柜（电伴热箱等）进线接线端子处。从变电所到成套电控柜（电伴热箱等）的进线动力电缆和控制电缆属于甲方设计及供货范围。成套电控柜到各用电设备的动力电缆和控制电缆，以及桥架、穿线管、安装支架等属于供货商设计及供货范围。 For the complete electric control cabinet (electric heat tracing box, etc.), the interface is at the incoming wiring terminal of the complete electric control cabinet (electric heat tracing box, etc.). The design and supply of incoming power cables and control cables from the substation to the complete electric control cabinet (electric tracing box, etc.) is in buyer’s scope. Meanwhile, The design and supply of power cables and control cables from complete electric control cabinet to each electrical equipment, as well as cable tray(if needed), conduit, installation bracket, etc. is in vendor’s scope. | TCC | [5 empty] | Design OK but not supply Please refer to our technical offer | 2024-10-04 | 2024.10.14 TCC：The battery limit is the electrical control cabinet. Except for the power supply and the incoming cable of electrical control cabinet, others belongs to the vendor. Please provide technical proposal and optional quotation as request.
2 |  |  | 电源电压要求： Power supply voltage requirements: P≥500kW 6kV 3 相 3 线 50Hz 10kV 3P 3W 50Hz P＜500kW 400V 3 相 3 线 50Hz 400V 3P 3W 50Hz 电动阀（MOV） 400V 3 相 4 线 50Hz 380V 3P 4W 50Hz 单相设备single phase equipment 230V 1 相 3 线 50Hz 230V 1P 3W 50Hz | TCC | [5 empty] | OK | 2024-10-04
3 |  |  | 若厂家有特殊供电电源要求，例如直流或UPS供电，必须和买方声明并提供用电负荷清单。 If the seller has special power supply requirements, such as DC or UPS power supply, it must declare with the buyer and provide the power supply load list. | TCC | [5 empty] | OK | 2024-10-04
4 |  |  | 防护等级要求详见成套设备电气技术规定“ELE-7G02-00-70-011-SPE Packaged Equipment Electrical Requirements”5.4.8节。 The minimum degree of protection of enclosures (IP and IK codes respectively as per GB/T 4208 and GB/T 20138) of the electrical equipment and material shall comply with part 5.4.8 of ELE-7G02-00-70-011-SPE Packaged Equipment Electrical Requirements. | [6 empty] | Hasler standards : - Electrical Control cabinet : IP55 - Local Control Panel : IP66 - Jonction box : IP66 - Frequency variator : IP2x - Electric motor : IP55 | 2024-10-04 | 2024.10.14 TCC：Noted.
5 |  |  | 户外成套电控柜（箱）、电气设备需满足最低环境温度-33.4℃要求。具体要求详见请购文件里的环境温度条件。 The minimum ambient temperature to select outdoor Instrument/ Electrical/ Telecom equipments is -33.4°С. For specific requirements, please refer to the ambient temperature conditions in the requisition documents. | TCC | [5 empty] | Deviated subject | 2024-10-04 |  |  | open
6 |  |  | 成套电控柜（电伴热箱等）应为下进线下出线方式。防护等级不低于IP55, 防爆等级应满足现场要求。当其位于露天场所应配置三包围的防雨罩。 Complete sets of electric control cabinets (electric heat tracing box, etc.) should be with inlet and outlet from the bottom side. The protection level is not less than IP55, and the explosion-proof level should meet the site requirements. When it is located in an open place, it should be equipped with a three-surrounded rain cover. | TCC | [5 empty] | Please confirm the area is non-hazardous area | 2024-10-04 | 2024.10.14 TCC：Confirm, there is non-hazardous area.
7 |  |  | 电机应能在下述系统变化情况下提供额定输出功率： 电压波动： ±5 % (GB/T 755) 频率波动： ±5% 频率和电压组合波动： ±5% Motors shall be capable of providing their rated output under system variations as stated below: Voltage range: ±5 % (GB/T 755) Frequency range: ±5 % Combined frequency and voltage range: ±5 % | TCC | [5 empty] | OK | 2024-10-04
8 |  |  | 所有电动机采用高效节能产品。高低压电机满足 GB30254-2013 和 GB18613-2020 中的能效 2 级要求。 All motors shall be high energy-efficiency type. MV/LV motors meet the energy efficiency grade 2 requirements in GB30254-2013 and GB18613-2020 | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
9 |  |  | 电机选用原则：所有室外安装的电机整体防护等级均要求不低于 IP55。 The minimum protection degree for all outdoor installation motors shall be IP55 | TCC | [5 empty] | OK | 2024-10-04
10 |  |  | 调速电机应选用变频专用电机。 Dedicated VFD motors shall be used with the speed control required. | TCC | [5 empty] | To be discussed following customer process | 2024-10-04 |  |  | open
11 |  |  | 电机接线盒应符合以下技术要求： 1. 防护等级不低于 IP55. 2. 空间加热器和其他辅助设备的连接应引入单独的辅助接线盒。主接线盒内应有一个接地端子，用于将电缆屏蔽层接地。 3. 接线盒应位于面向联轴器底部的右侧或顶部。供应商的图纸应显示接线盒的实际位置。 Terminal boxes shall be large enough to allow the easy connection of the supply cables. 1. Terminal boxes shall have mechanical protection not less than IP55. 2. Connections of space-heaters and other auxiliary devices shall be brought out into separate auxiliary terminal boxes. Inside the main terminal box an earthing terminal shall be provided for earthing the cable shields. 3. Unless otherwise specified, terminal boxes shall be located on the right side facing coupling end, or on the top. Vendor's drawings shall show the actual location of terminal boxes. | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
12 |  |  | 振动和噪声： 振动和噪声应满足GB/T10068，GB/T10069内相关规定 Vibration and Noise: Unless otherwise specified, vibration and noise levels shall not exceed the limits shown in GB/T 10068 and GB/T 10069. | TCC | [5 empty] | To be clarified | 2024-10-04 |  |  | open
13 |  |  | 在潮湿环境中间歇工作的室外电机，以及 185 千瓦以上的电机应安装空间加热器。 Outdoor installed motors for intermittent duty in moisty ambient, and motors above 185 kW shall be fitted with space heaters | TCC | [5 empty] | OK | 2024-10-04
14 |  |  | 电机热敏电阻满足统一规定ELE-7G02-00-70-010中6.5节技术要求 Thermoresistances shall be according to part 6.5 of ELE-7G02-00-70-010 Specification for Induction Motors | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
15 |  |  | 电机接线盒一侧和主接线盒内应有接地螺栓。顶部安装接线盒的电机应在两侧都有接地螺栓。 Ground bolts shall be provided on terminal box side of the frame and inside the main terminal box. Motors with top-mounted terminal box shall have ground bolts on both sides. | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
16 |  |  | 电机格兰由卖方提供。电机接口采用电缆密封接头（格兰头）连接，材质黄铜镀镍，防护等级 IP65，防爆等级应满足现场要求。买方提供电缆外径等参数。 Motor gland should be provided by seller. The terminal box of the motor shall be connected by the cable gland. Material of the cable gland shall be nickel plated brass with protection degree of IP65, explosion-proof grade shall meet site requirements. Buyer will provide parameters of cable diameter. | TCC | [5 empty] | OK | 2024-10-04
17 |  |  | 对于铠装电缆，采用铠装电缆专用格兰头（带接地环）。 For armored cables, use armored cable special gran head (with ground ring). | TCC | [5 empty] | Cable to be supply by customer | 2024-10-04 | 2024.10.14 TCC：Vendor supply cable gland which is with ground wing.
18 |  |  | 成套电控柜内的计量表计（互感器，多功能表计）需提供哈萨克斯坦 PAC 证书及配套文件（类型描述和标定方法）并提交天辰项目组审核 The measuring meter (CT, PT, multifunctional meter) in the complete electric control cabinet(box) shall provide Kazakhstan PAC certificate and supporting documents (type description and calibration method) and submit to Tian chen Project team for review. | TCC | [5 empty] | Deviated subject | 2024-10-04 |  |  | open
19 |  |  | 电气设备、材料的设计选择应执行GB国标规范，详见电气统一规定ELE-7G02-00-70-001-SPE Electrical Design Guidelines里的第4章节GB国标规范。 The design and selection of Electrical equipment and materials shall comply with GB national standard specifications, as detailed in Chapter 4-GB National Standard Specifications in ELE-7G02-00-70-001-SPE Electrical Design Guidelines. | TCC | [5 empty] | Deviated subject | 2024-10-04 |  |  | open
20 |  |  | 成套设备分供元件应在采购要求的分供方品牌中选取。 Sub-supplied component of electrical equipment shall be selected from among the brands of sub-AVL required by the buyer‘s procurement. | TCC | [5 empty] | Please provide sub-supplier list | 2024-10-04 | 2024.10.14 TCC：Please kindly check TCC procurement document.
21 |  |  | 供货商提供图纸及相关资料需要符合统一规定要求 Drawings and relevant information provided by the supplier (select and use according to the actual equipment) | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
22 |  |  | 成套设备和电机具体要求详见成套设备电气技术规定“ELE-7G02-00-70-011-SPE Packaged Equipment Electrical Requirements”和电机技术规格书“ELE-7G02-00-70-010 Specification for Induction Motors”。 For detailed Requirements of complete Equipment and motors, please refer to the "ELE-7G02-00-70-011-SPE Packaged Equipment Electrical Requirements" and the motor technical specification "ELE-7G02-00-70-010" Specification for Induction Motors ". | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
|  |  | ”ELE-7G02-00-70-010_0_0_EN_IFF Specification for Induction Motors“为电气统一规定，请供应商执行。 | TCC | [5 empty] | To be discussed later | 2024-10-04 |  |  | open
|  |  | Electrical major updated the new version of chapter 5.5.2 in “Packaged Equipment Electrical Requirements” ,see attachment "【20241028】ELE-7G02-00-70-011-SPE_0_1_EN_IFF Packaged Equipment Electrical Requirements." 电气更新了新版的统一规定中的5.5.2，见附件【20241028】ELE-7G02-00-70-011-SPE_0_1_EN_IFF Packaged Equipment Electrical Requirements. | TCC | [6 empty] | 2024-10-14 |  |  | open
1. For "Vendor Reply" row, A --- Comply, B --- Not Comply, C --- Comply with Cost Effects, D --- Comply with Deviation/Exception
2. If B/C/D is selected or N.A. for A/B/C/D please also fill "Vendor's Proposal" row