## Equipment
EQUIPMENT LIST
[8 empty] | PROJECT NUMBER: | 7701
[8 empty] | PROJECT TITLE: | OTO, Gelsa, Spain
[8 empty] | COMPANY: | SAINT-GOBAIN
Line-Process area number | Separator [ _ ] | Equipment number | Equipment Descriptor | Separator [ _ ] | Sub-comp. items number | Equipment | ELD/P&ID (short form, e.g E10-001) | S-G Tag | Supplier Tag | Description | Commissioning Level | Principal Parameter [Range, Size etc] | Manufacturer | Model Family/Type | Model Number | Electrical I/O Data | Power [kW] | Voltage [V] | AC (Volt) | DC (Volt) | Frequency [Hz] | Config 87Hz? (Special drives) | Control [DOL, VFD etc] | Signal to PLC (Discrete, 4..20mA, PA,DP etc) | Normally Open/Close [NO/NC] | Single acting sol. [Open/Close] | Double acting sol. | Atex zone | Safety system component | Motor Speed [1/min] | Max Speed [m/min] | Max Time Expect [s] | Electrical Drawing Number | UPS Required | Sensor Technology | Piping/Valve Data | Material | NB/DN [mm] | ID [mm] | OD [mm] | Length (estimate) [m] | Qty bends | Connection (End1 or ALL) | Connection (End2) | Fluid Type | Fluid Viscosity [UNITS?] | Design Presure [barg] | Temperature Min-Nom-Max [°C] | Velocity [m/s] | Actuator | Position switch | Insulation &/or trace heating | Other Specifications | Tank/ Silo Data | Tank/Silo Height [m] | Tank/Silo Diameter [m] | Tank Internal Volume [m3] | High Level Switch Height [m] | Low Level Switch Height [m] | Agitator requirement [m] | Silo Capacity [m3] | Silo Capacity [T] | Utility connection required [Compressed air, gas, water] | Physical Data | Floor level [m] | Estimated Mass [kg] | Approximate Packing Length [m] | Appoximate Packing Width [m] | Approximate Packing Height [m] | Accessories | Supplier | Design Status | Remarks | Revision # | (a)dded/ (d)eleted/ (r)evised
Note - where no information is shown data is to be confirmed.
ZC50- Slurry Filtering System | [7 empty] | EQUIPMENT ON ELD 10190-C50-DEL-GMT-001 Slurry Dewatering
ZC50 | _ | 001 | INS | _ | FT01 | Instrument | C00-001 | AC50_156INS_FT1 | Other (TBC) | Slurry Inlet Flow Transmitter | 3 | Magnetic type, 40-60 m3/h @ 6 barg - 100°C -1400Kg/m3, DN65 (2 1/2") (with flanges DN100 = 4"), in-line vertical mounting, accuracy 0.2%, PA profibus, 24VDC (note: no grounding rings required for SS pipes) | Other (TBC) | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [12 empty] | Stainless Steel | DN25 | [35 empty] | I
ZC50 | _ | 002 | SLY | _ | 100S1 | Piping | C00-001 | ZC50_002SLY_100S1 | Other (TBC) | Slurry Inlet Flexible Piping | 3 | DN 100mm - OD mm - Length See DRG as per GMT drawing 10190-C50-DMF-GMT-XXX | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100 |  |  | See DRG | TBC | Flanged | Flanged | Stucco Slurry |  | 3 barg | 85-95-110 |  |  |  | 25 mm Rockwool | [21 empty] | F
ZC50 | _ | 003 | VAO |  |  | Valve | C00-001 | ZC50_003VAO | Other (TBC) | Filter Belt Inlet Actuated Valve | 3 | Ball valve DN100 stainless steel, FO (Fail safe to Open) with Spring Return Actuator, flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100 |  |  |  |  | Flanged | Flanged | Stucco Slurry |  | 3 barg | 85-95-110 |  | Yes | Yes | 25 mm Rockwool
ZC50 | _ | 003 | VAO | _ | SOV01 | Instrument | C00-001 | ZC50_003VAO_SOV01 | Other (TBC) | Filter Belt Inlet Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Other (TBC) | TBC | TBC | Y |  | 24 |  | X | [5 empty] | X | [10 empty] | Stainless Steel | - |  | - |  |  | Valve | None | - | - | - | -
ZC50 | _ | 003 | INS | _ | ZS01 | Instrument | C00-001 | ZC50_003INS_ZS01 | Other (TBC) | Filter Belt Inlet Actuated Valve Position Sensor 1 | 3 | Mounted limit switch box; IP65; 2 micro switches; suitable for actuator; switching capacity 4A/250VAC-1A/24VDC | Other (TBC) | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 003 | INS | _ | ZS02 | Instrument | C00-001 | ZC50_003INS_ZS02 | Other (TBC) | Filter Belt Inlet Actuated Valve Position Sensor 2 | 3 | Linked to ZC50_003INS_ZS01 | Other (TBC) | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 005 | SLY | _ | 100S1 | Piping | C00-001 | ZC50_005SLY_100S1 | Filter Belt Supplier | Filter Belt Inlet Piping | 3 | DN 100mm - OD mm - Length See DRG as per GMT drawing 10190-C50-DMF-GMT-XXX | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100 |  |  | See DRG | TBC | Flanged | Flanged | Stucco Slurry |  | 3 barg | 75-85-95 |  |  |  | 25 mm Rockwool | [21 empty] | F
ZC50 | _ | 015 | VAO |  |  | Valve | C00-001 | ZC50_015VAO | Filter Belt Supplier | Filter Belt Tension Roller Actuated Valve | 3 | Ball valve DNTBC stainless steel, FO (Fail safe to Open) with Single Acting Spring Return Actuator, flanged | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | TBC |  |  |  |  | Flanged | Flanged | Process Water |  | 3 barg | 25-50-80 |  | Yes | Yes
ZC50 | _ | 015 | BLT | _ | SOV01 | Instrument | C00-001 | ZC50_015BLT_SOV01 | Filter Belt Supplier | Filter Belt Tension Roller Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [5 empty] | X | [10 empty] | Stainless Steel | - |  | - |  |  | AE10_215VAO | None | - | - | - | -
ZC50 | _ | 020 | BLT |  |  | Equipment | C00-001 | ZC50_020BLT | Filter Belt Supplier | Vaccuum Filter Belt Equipment | 1 | Multi-zone continuous Filter Belt with Vacuum moisture removal, belt cleaning and dual washing capacity. Throughput- 28 t/h Gypsum, ~55000 l/h slurry Dimensions- TBC Weight - TBC | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 020 | BLT |  |  | Equipment | C00-001 | ZC50_020BLT | Filter Belt Supplier | Vaccuum Filter Belt Equipment - Filter Belts | 3 | Continuous Dual belts, specifics TBC by Supplier | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 020 | BLT |  |  | Equipment | C00-001 | ZC50_020BLT | Filter Belt Supplier | Vaccuum Filter Belt Equipment - Installation Equipment | 3 | Installation items for Vaccuum Filter Belt (See 10190-C50-TDS-GMT-001), as well as Ancillary items such as insulation and wiring. | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 020 | BLT | _ | M01 | Motor | C00-001 | ZC50_020BLT_M01 | Filter Belt Supplier | Vacuum Filter Belt Equipment Motor | 3 | 400V, 3Ph, 50 Hz, efficiency IE2, 1500RPM, TBC kW | Filter Belt supplier | TBC | TBC | Y | TBC | 400 | X |  |  |  | VFD | Profibus PA | [12 empty] | Stainless Steel | [7 empty] | Stucco Slurry | 3-10 Centipoise | 5 barg | 70-90-100 | [25 empty] | I
ZC50 | _ | 020 | INS | _ | SS01 | Instrument | C00-001 | ZC50_020INS_SS01 | Filter Belt Supplier | Vaccuum Filter Belt Speed Sensor 1 | 3 | Speed Sensor, accuracy XX | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | BLT | _ | STB01 | Equipment | C00-001 | ZC50_020BLT_STB01 | Filter Belt Supplier | Vacuum Filter Belt Equipment - Belt Tracking (Left) | 3 | Belt Tracking System (Left), pneumatically Driven | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 020 | BLT | _ | STB02 | Equipment | C00-001 | ZC50_020BLT_STB02 | Filter Belt Supplier | Vacuum Filter Belt Equipment - Belt Tracking (Right) | 3 | Belt Tracking System (Right), pneumatically Driven | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 020 | INS | _ | ZS01 | Instrument | C00-001 | ZC50_020INS_ZS01 | Filter Belt Supplier | Vacuum Filter Belt Alignment Sensor 1 | 3 | Mounted Inductive Limit switch (Left); IP65; 1 switch; 24VDC , linked with ZC50_020BLT_STB01 | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | INS | _ | ZS02 | Instrument | C00-001 | ZC50_020INS_ZS02 | Filter Belt Supplier | Vacuum Filter Belt Alignment Sensor 2 | 3 | Mounted Inductive Limit switch (Left); IP65; 1 switch; 24VDC , linked with ZC50_020BLT_STB02 | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | INS | _ | ZS03 | Instrument | C00-001 | ZC50_020INS_ZS03 | Filter Belt Supplier | Vacuum Filter Belt Alignment Sensor 3 | 3 | Mounted Inductive Limit switch (Left); IP65; 1 switch; 24VDC | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | INS | _ | ZS04 | Instrument | C00-001 | ZC50_020INS_ZS04 | Filter Belt Supplier | Vacuum Filter Belt Inlet Position Switch 1 | 3 | Mounted Inductive Limit switch (Left); IP65; 1 switch; 24VDC | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | INS | _ | ZS05 | Instrument | C00-001 | ZC50_020INS_ZS05 | Filter Belt Supplier | Vacuum Filter Belt Inlet Position Switch 2 | 3 | Mounted Inductive Limit switch (Left); IP65; 1 switch; 24VDC | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC50 | _ | 020 | INS | _ | SS02 | Instrument | C00-001 | ZC50_020INS_SS02 | Filter Belt Supplier | Vaccuum Filter Belt Rupture Limit Switch | 3 | Mounted limit switch; IP65; 1 micro switch; 24VDC , Connected to ZC50_015BLT_SOV01 | Filter Belt supplier | TBC | TBC | Y |  | 24 |  | X
ZC50 | _ | 020 | BLT | _ | VNT | Equipment | C00-001 | ZC50_020BLT_VNT | Filter Belt Supplier | Vaccuum Filter Belt Vent Structure | 3 | Cover Hood SS 316, split into 10 Sections over the Belt Filter Length. Supported from Belt Frame, connects to ZC50_035FAN | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | [7 empty] | Stucco Slurry | 3-10 Centipoise | 5 barg | 70-90-100
ZC50 | _ | 020 | BLT | _ | MT01 | Equipment | C00-001 | ZC50_020BLT_MT01 | Filter Belt Supplier | Vaccuum Filter Belt Moisture Sensor | 3 | Colour or similar type Moisture sensor transmitter capable of continuous reading of moving product. | Moisture Transmitter Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profinet | [12 empty] | Stainless Steel | [7 empty] | Stucco Slurry | 3-10 Centipoise | 5 barg | 70-90-100 | [25 empty] | J
ZC50 | _ | 020 | TNK | _ | LT01 | Instrument | C00-001 | ZC50_020TNK_LT01 | Filter Belt Supplier | Filter Belt Inlet Level Transmitter 1 | 3 | Laser Level Transmitter, accuracy 0.1 %, 24 V DC, Profibus PA/Ethernet connection. Mounting unit. | Skids Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [49 empty] | F
ZC50 | _ | 020 | TNK | _ | LT02 | Instrument | C00-001 | ZC50_020TNK_LT02 | Filter Belt Supplier | Filter Belt Inlet Level Transmitter 2 | 3 | Laser Level Transmitter, accuracy 0.1 %, 24 V DC, Profibus PA/Ethernet connection. Mounting unit. | Skids Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [49 empty] | F
ZC50 | _ | 020 | TNK | _ | LT03 | Instrument | C00-001 | ZC50_020TNK_LT03 | Filter Belt Supplier | Filter Belt Outlet Level Transmitter 1 | 3 | Laser Level Transmitter, accuracy 0.1 %, 24 V DC, Profibus PA/Ethernet connection. Mounting unit. | Skids Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [49 empty] | F
ZC50 | _ | 020 | TNK | _ | LT04 | Instrument | C00-001 | ZC50_020TNK_LT04 | Filter Belt Supplier | Filter Belt Outlet Level Transmitter 2 | 3 | Laser Level Transmitter, accuracy 0.1 %, 24 V DC, Profibus PA/Ethernet connection. Mounting unit. | Skids Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [49 empty] | F
ZC50 | _ | 021 | VAM |  |  | Valve | C00-001 | ZC50_021VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 1 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 022 | VAM |  |  | Valve | C00-001 | ZC50_022VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 2 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 023 | VAM |  |  | Valve | C00-001 | ZC50_023VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 3 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 024 | VAM |  |  | Valve | C00-001 | ZC50_024VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 4 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 025 | VAM |  |  | Valve | C00-001 | ZC50_025VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 5 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 026 | VAM |  |  | Valve | C00-001 | ZC50_026VAM | Filter Belt Supplier | Vaccuum box Manual Isolation Valve 6 | 3 | Manual Butterfly Valve, DN150 wafer connection | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150 |  |  | - | - | Flanged | Flanged | Process Water |  | 40 bar | 25-50-80 | [22 empty] | MIVAL ART 347 |  |  | F
ZC50 | _ | 027 | FIL | _ | 500S1 | Piping | C00-001 | ZC50_027FIL_500S1 | Filter Belt Supplier | Filter Belt Filtrate Collection Piping | 3 | DN 500mm - OD mm - Length See DRG as per GMT drawing 10190-C50-DMF-GMT-XXX | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 500 |  |  | See DRG | TBC | Flanged | Flanged | Stucco Slurry |  | 3 barg | 75-85-95 |  |  |  | 25 mm Rockwool | [21 empty] | F
ZC50 | _ | 028 | FIL | _ | 450S1 | Piping | C00-001 | ZC50_028FIL_450S1 | Filter Belt Supplier | Filter Belt Filtrate Transfer Piping | 3 | DN 450mm - OD mm - Length See DRG as per GMT drawing 10190-C50-DMF-GMT-XXX | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 450 |  |  | See DRG | TBC | Flanged | Flanged | Stucco Slurry |  | 3 barg | 75-85-95 |  |  |  | 25 mm Rockwool | [21 empty] | F
ZC50 | _ | 031 | VNT | _ | 250S1 | Piping | C00-001 | ZC50_031VNT_250S1 | Filter Belt Supplier | Vaccuum Filter Belt Vent Piping | 3 | DN 250mm - OD mm - Length 10 m as per GMT drawing 10190-C50-DMF-GMT-XXX, Links to Emission Vent VTC.01 | Filter Belt supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 250 |  |  | 10 m | 8 | Flanged | Flanged | Stucco Slurry |  | 3 barg | 75-85-95 |  |  |  | 25 mm Rockwool
ZC50 | _ | 035 | FAN |  |  | Equipment | C00-001 | ZC50_035FAN | Filter Belt Supplier | Vaccuum Filter Belt Vent Fan | 3 | Filter Belt Vent Fan, | Filter Belt supplier | TBC | TBC | N
ZC50 | _ | 035 | FAN | _ | M01 | Motor | C00-001 | ZC50_035FAN_M01 | Filter Belt Supplier | Vaccuum Filter Belt Vent Fan Motor | 3 | 400V, 3Ph, 50 Hz, efficiency IE2, 1500RPM, 30 kW | Filter Belt supplier | TBC | TBC | Y | 30 | 400 | X |  |  |  | VFD | [13 empty] | Stainless Steel | [7 empty] | Stucco Slurry | 3-10 Centipoise | 5 barg | 70-90-100
ZC50 | _ | 101 | VAM |  |  | Valve | C00-001 | ZC50_101VAM | Other (TBC) | Wash Water Storage Tank Inlet Isolation Valve | 3 | Full Bore Ball Valve DN100, Flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100 | [35 empty] | I
ZC50 | _ | 102 | WTR | _ | 040S1 | Piping | C00-001 | ZC50_102WTR_040S1 | Other (TBC) | Wash Water Fresh Water Inlet Piping | 3 | DN 100mm - OD mm - Length See DRG as per GMT drawing 7701-C50-DMF-GMT-XXX | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100 |  |  | See DRG | TBC | Flanged | Flanged | Stucco Slurry |  | 3 barg | 75-85-95 |  |  |  | 25 mm Rockwool | [21 empty] | H
ZC50 | _ | 103 | VAO |  |  | Instrument | C00-001 | ZC50_103VAO | Other (TBC) | Wash Water Fresh Water Inlet Actuated Valve | 3 | Ball valve DN100 stainless steel, FC (Fail safe to close) with Spring Return Actuator, flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100 |  |  |  |  | Flanged | Flanged | Process Water |  | 3 barg | 25-50-80 |  | Yes | Yes
ZC50 | _ | 103 | VAO | _ | SOV01 | Instrument | C00-001 | ZC50_103VAO_SOV01 | Other (TBC) | Wash Water Fresh Water Inlet Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Other (TBC) | TBC | TBC | Y |  | 24 |  | X | [5 empty] | X | [10 empty] | Stainless Steel | - |  | - |  |  | AE10_215VAO | None | - | - | - | -
ZC50 | _ | 103 | INS | _ | ZS01 | Instrument | C00-001 | ZC50_103INS_ZS01 | Other (TBC) | Wash Water Fresh Water Inlet Actuated Valve Position Sensor 1 | 3 | Mounted limit switch box; IP65; 2 micro switches; suitable for actuator; switching capacity 4A/250VAC-1A/24VDC SOV01 | Other (TBC) | TBC | TBC | Y |  | 24 |  | X
ZC50 | _ | 103 | INS | _ | ZS02 | Instrument | C00-001 | ZC50_103INS_ZS02 | Other (TBC) | Wash Water Fresh Water Inlet Actuated Valve Position Sensor 2 | 3 | Linked to ZC50_103INS_ZS01 | Other (TBC) | TBC | TBC | Y |  | 24 |  | X
ZC50 | _ | 103 | INS | _ | FRL | Instrument | C00-001 | ZC50_103INS_FRL | Other (TBC) | Wash Water Actuated Valve Filter Regulator | 3 | Compressed Air Filter Regulator with gauge, Normal working pressure 4 barg, port BSP 1/4", capacity: see reference, orientation: Right to Left | Other (TBC) | TBC | TBC | N | [57 empty] | C
ZC50 | _ | 120 | TNK |  |  | Tank | C00-001 | ZC50_120TNK | Other (TBC) | Wash Water Storage Tank | 2 | preliminary data consider Tank Drawing when issued D = 2.3 m, H= 2.6 m Top: 6 flanges (1 Agitator Flange (Min 300 mm) + 1 Fresh Water Feed (DN100) + 1 Filtered Water Feed (DN100) + 1 Recycle Inlet (DN100) + 1 Level Transmitter (DN50) + 1 Spare Flanges (DN50)) + 1 top standard 350mm diameter Inspection Hatch Side: 1 Flange (1 Main Outlet (DN80)) + 2 Level Switches (G 1/2") + 1 side standard 800mm diameter Access Hatch Bottom: Inclined base (30 %) to middle of tank, with DN100 drain Flange connection. All outlets and inlets flanged. Spare/Drain connections to be delivered with blind flanges. | Other (TBC) | TBC | TBC | N
ZC50 | _ | 120 | AGI |  |  | Equipment | C00-001 | ZC50_120AGI | Other (TBC) | Wash Water Storage Tank Agitator | 3 | reduced speed ~ 400rpm, excentric mounting, shaft diam 50mm, shaft length 2100mm, wetted material SS304 |  | TBC | TBC | N
ZC50 | _ | 120 | AGI | _ | M01 | Instrument | C00-001 | ZC50_120AGI_M01 | Other (TBC) | Wash Water Storage Tank Agitator Motor | 3 | 400,V, 3Ph, 50 Hz, high efficiency IE3, 1500 RPM,5.5, kW |  | TBC | TBC | Y | 5.5 | 400 |  |  |  |  | VFD
ZC50 | _ | 120 | TNK | _ | LT01 | Instrument | C00-001 | ZC50_120TNK_LT01 | Other (TBC) | Wash Water Storage Tank Level Transmitter | 3 | Radar Level Transmitter @ 80GHz, 24 V DC Profibus PA, with flanged connection DN50 | Other (TBC) | TBC | TBC | Y |  | 24 |  | X |  |  |  | 4..20mA | [49 empty] | F
ZC50 | _ | 120 | TNK | _ | LS01 | Instrument | C00-001 | ZC50_120TNK_LS01 | Other (TBC) | Wash Water Storage Tank High Level Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC Thread BSP 1/2", 316L | Other (TBC) | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA
ZC50 | _ | 120 | TNK | _ | LS02 | Instrument | C00-001 | ZC50_120TNK_LS02 | Other (TBC) | Wash Water Storage Tank Low Level Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC Thread BSP 1/2", 316L | Other (TBC) | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA
ZC50 | _ | 127 | VAM |  |  | Valve | C00-001 | ZC50_127VAM | Other (TBC) | Wash Water Storage Tank Drain Valve | 3 | Full Bore Ball Valve DN100, Flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC50 | _ | 129 | VAM |  |  | Valve | C00-001 | ZC50_129VAM | Other (TBC) | Wash Water Storage Tank Outlet Valve | 3 | Full Bore Ball Valve DN80, Flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 130 | WTR | _ | 080S1 | Piping | C00-001 | ZC50_130WTR_080S1 | Other (TBC) | Wash Water Feed Piping | 3 | DN 80mm - OD mm - Length as per GMT drawing 10190-C50-DMF-GMT-XXX | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 147 | WTR | _ | 032S1 | Piping | C00-001 | ZC50_147WTR_032S1 | Other (TBC) | SKID01WSH Internal Piping | 3 | DN 80mm - OD mm - Length As per SKID01WSH | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 150 | PMP |  |  | Pump | C00-001 | ZC50_150PMP | Other (TBC) | SKID01WSH Pump | 2 | 334 l/min @ 6 Bar Connections: flanges Inlet: DN80 Outlet: DN80 speed XXX rpm @ 50 Hz frequency range XX-50 Hz | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 32
ZC50 | _ | 150 | PMP | _ | M1 | Motor | C00-001 | ZC50_150PMP_M1 | Other (TBC) | SKID01WSH Pump Motor | 3 | 400V, 3Ph, 50 Hz, efficiency IE2, 1500RPM, TBC kW | Other (TBC) | TBC | TBC | Y | TBC | 400 | X |  |  |  | VFD
ZC50 | _ | SKID01 | WSH |  |  | SKID | C00-001 | ZC50_SKID01WSH | Other (TBC) | SKID01WSH - Skid Materials & Assembly | 2 | SKID001WSH Stainless steel frame, as per DWG (10190-C00-DRG-GMT-XXX), as well as assembly of all internal instruments, valves and piping related to the skid. | Other (TBC) | TBC | TBC | N
ZC50 | _ | SKID01 | WSH |  |  | SKID | C00-001 | ZC50_SKID01WSH | Other (TBC) | SKID01WSH - Assembly Labour & Workshop Equipment | 3 | Workshop Equipment and Manpower Labour required to construct SKID01WSH | Other (TBC) | TBC | TBC | N
ZC50 | _ | SKID01 | WSH |  |  | SKID | C00-001 | ZC50_SKID01WSH | Other (TBC) | SKID01WSH - Installation & Ancillary Materials | 3 | Installation items for SKID01WSH (See 10190-C00-TDS-GMT-001), as well as Ancillary items such as insulation and wiring. | Other (TBC) | TBC | TBC | N
ZC50 | _ | 150 | VAP |  |  | Valve | C00-001 | ZC50_150VAP | Other (TBC) | SKID01WSH Pressure Relief Valve | 3 | Pressure Relief Valve DN25(1") (process side) x DN40 (1 1/2") (discharge side) (connection sizes TBC by skid supplier), Stainless Steel, Spring-Loaded Type. Maximum working pressure = 3 barg; valve set to relieve at 4.5 barg. | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 25 | [35 empty] | H
ZC50 | _ | 151 | VAM |  |  | Valve | C00-001 | ZC50_151VAM | Other (TBC) | SKID01WSH Outlet Manual Isolation Valve | 3 | Full Bore Ball Valve DN80, Flanged | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 152 | WTR | _ | 080S1 | Piping | C00-001 | ZC50_152WTR_080S1 | Other (TBC) | SKID01WSH Outlet Piping | 3 | DN 80mm - OD mm - Length as per GMT drawing 7701-C50-DMF-GMT-XXX | Other (TBC) | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 154 | VAM |  |  | Valve | C00-001 | ZC50_154VAM | Filter Belt Supplier | Wash Water Inlet Manual Isolation Valve | 3 | Full Bore Ball Valve DN80, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 156 | INS | _ | FT01 | Instrument | C00-001 | AC50_156INS_FT1 | Filter Belt Supplier | Belt Filter Wash Water Flow Transmitter | 3 | Magnetic type, 100-350 l/min @ 6 barg - 80°C -1000Kg/m3, DN50 (2") (with flanges DN80 = 3"), in-line vertical mounting, accuracy 0.2%, PA profibus, 24VDC (note: no grounding rings required for SS pipes) | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | Profibus PA | [13 empty] | 80 | [35 empty] | I
ZC50 | _ | 157 | VAM |  |  | Valve | C00-001 | ZC50_157VAM | Filter Belt Supplier | Belt Filter Wash Water Pressure Indicator Isolation Valve | 3 | Full Bore Ball Valve DN15, Flanged | Filter Belt Supplier | TBC | TBC | N | [21 empty] | 15
ZC50 | _ | 157 | INS | _ | PI01 | Instrument | C00-001 | AC50_157INS_PI1 | Filter Belt Supplier | Belt Filter Wash Water Pressure Indicator | 3 | Pressure Gauge Assembly complete Syphon and Gauge cock. DN15 Threaded connection 100 mm dial orientated based on layout requirements | Filter Belt Supplier | TBC | TBC | N | [21 empty] | 15
ZC50 | _ | 158 | VAO |  |  | Valve | C00-001 | ZC50_158VAO | Filter Belt Supplier | Spray Water Actuated Valve | 3 | Diaphragm valve DN80 Coated Aluminium, Control Pressure- 4.5 Bar FC (Fail safe to close) with Spring Return Actuator, flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 80
ZC50 | _ | 158 | VAO | _ | SOV01 | Instrument | C00-001 | ZC50_158VAO_SOV01 | Filter Belt Supplier | Spray Water Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [5 empty] | X
ZC50 | _ | 158 | INS | _ | ZS01 | Instrument | C00-001 | ZC50_158INS_ZS01 | Filter Belt Supplier | Spray Water Actuated Valve Position Switch 1 | 3 | Mounted limit switch box; IP65; 2 micro switches; suitable for actuator; switching capacity 4A/250VAC-1A/24VDC SOV01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X
ZC50 | _ | 158 | INS | _ | ZS02 | Instrument | C00-001 | ZC50_158INS_ZS02 | Filter Belt Supplier | Spray Water Actuated Valve Position Switch 2 | 3 | Linked to ZC50_158INS_ZS01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X
ZC50 | _ | 158 | INS | _ | FRL | Instrument | C00-001 | ZC50_158INS_FRL | Filter Belt Supplier | Spray Water Actuacted Valve Filter Regulator | 3 | Compressed Air Filter Regulator with gauge, Normal working pressure 4.5 barg, port BSP 1/4", capacity: see reference, orientation: Right to Left (Applies to both 3-Way Valve and the Pressure Regulator AC50_284VAA) | Filter Belt Supplier | TBC | TBC | N | [57 empty] | C
ZC50 | _ | 159 | VAM |  |  | Valve | C00-001 | ZC50_159VAM | Filter Belt Supplier | Spray Water Bottom Spray Manual Isolation Valve | 3 | Butterfly Valve DN65, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65
ZC50 | _ | 160 | VAM |  |  | Valve | C00-001 | ZC50_160VAM | Filter Belt Supplier | Spray Water Top Spray Manual Isolation Valve | 3 | Full Bore Ball Valve DN65, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65
ZC50 | _ | 165 | SPY |  |  | Equipment | C00-001 | ZC50_165SPY | Filter Belt Supplier | Spray Water Spray Box | 3 | Stainless Steel 316 Spray box, with 4 spray nozzles (2 each sizes). Nozzle Piping size: DN65 Material collecting Drain: DN125 | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65/125
ZC50 | _ | 203 | INS | _ | PS01 | Instrument | C00-001 | ZC50_203INS_PS01 | Filter Belt Supplier | Main Unit Pressure Sensors | 3 | Pressure Sensor inside Pneumatic cabinet | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | 4..20mA
ZC50 | _ | 167 | WTR | _ | 125S1 | Piping | C00-001 | ZC50_167WTR_125S1 | Filter Belt Supplier | Spray Box Outlet Piping | 3 | DN 125mm - OD mm - Length as per GMT drawing 7701-C50-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 125
ZC51- Filter Belt Vacuum System | [7 empty] | EQUIPMENT ON ELD 10190-C00-DEL-GMT-001 Slurry Dewatering
ZC51 | _ | 003 | FIL | _ | 450S1 | Piping | C00-001 | ZC51_003FIL_450S1 | Filter Belt Supplier | Vacuum System Inlet Piping | 3 | DN 450mm - OD mm - Length as per GMT drawing 7701-C50-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 450 | [35 empty] | H
ZC51 | _ | 020 | CYC |  |  | Tank | C00-001 | ZC51_020CYC | Filter Belt Supplier | Vacuum System Separator | 2 | preliminary data consider Tank Drawing when issued D = 1 m, H= 2 m Top: 2 Flanges (1 Vacuum Outlet (DN450) + 1 Pressure Transmitter (DN50)) Side: 4 Flanges (1 Main Inlet (DN450), 1 flange for Level Switch Connection (DN50 with R 1" Lug Connection) + 1 side standard 800mm diameter Access Hatch Base: 2 Flanges (1 Filtrate Outlet (DN100), 1 flange for Level Switch Connection (DN25 with R 1 " Lug Connection) Spare/Drain connections to be delivered with blind flanges. | Filter Belt Supplier | TBC | TBC | N
ZC51 | _ | 020 | CYC | _ | LS01 | Instrument | C00-001 | ZC51_020CYC_LS01 | Filter Belt Supplier | Vacuum System Separator Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC R 1" Lug Connection, 316L | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 024 | VAM |  |  | Valve | C00-001 | ZC51_024VAM | Filter Belt Supplier | Vacuum System Separator PT Manual Isolation Valve | 3 | Full Bore Ball Valve DN25, Flanged one side, Threaded other side (PT) | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 25
ZC51 | _ | 024 | INS | _ | PT01 | Instrument | C00-001 | ZC51_024INS_PT01 | Filter Belt Supplier | Vacuum System Separator Pressure Transmitter | 3 | Capacitive Pressure Transmitter with Local Indicator, Connection- DN 50 Material- Ceramic | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | 4..20mA | [12 empty] | Ceramic | 50 | [35 empty] | I
ZC51 | _ | 027 | VAM |  |  | Valve | C00-001 | ZC51_027VAM | Filter Belt Supplier | Vacuum System Separator Outlet Manual Isolation Valve | 3 | Butterfly Valve DN100, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | GG25 | 100
ZC51 | _ | 027 | VAM |  |  | Valve | C00-001 | ZC51_027VAM | Filter Belt Supplier | Vacuum System Separator Drain Manual Isolation Valve | 3 | Butterfly Valve DN100, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | GG25 | 100
ZC51 | _ | 029 | WTR | _ | 050S1 | Piping | C00-001 | ZC51_029WTR_050S1 | Filter Belt Supplier | Vacuum System Separator Drain Piping | 3 | DN 100mm - OD mm - Length as per GMT drawing 7701-C50-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC51 | _ | 041 | WTR | _ | 032S1 | Piping | C00-001 | ZC51_041WTR_032S1 | Filter Belt Supplier | Vacuum System Separator Outlet Piping | 3 | DN 100mm - OD mm - Length as per GMT drawing 7701-C50-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC51 | _ | 050 | PMP |  |  | Pump | C00-001 | ZC51_050PMP | Filter Belt Supplier | Vacuum System Separator Pump | 2 | Self sucking Radial Pump 100-400 l/min @ 6 Bar Connections: flanges Inlet: DN100 Outlet: DN100 speed XXX rpm @ 50 Hz frequency range XX-50 Hz | Filter Belt Supplier | TBC | TBC | N
ZC51 | _ | 050 | VAO |  |  | Equipment | C00-001 | ZC51_050VAO | Filter Belt Supplier | Vacuum Pump Control Actuated Valve | 3 | Butterfly valve DN50 stainless steel, FC (Fail safe to close) with Double Acting Spring Return Actuator, flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Coated Alumninium | 50 | [35 empty] | I
ZC51 | _ | 050 | VAO | _ | SOV01 | Instrument | C00-001 | ZC51_050VAO_SOV01 | Filter Belt Supplier | Vacuum Pump Control Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 054 | VAM |  |  | Valve | C00-001 | ZC51_054VAM | Filter Belt Supplier | Vacuum System Separator Outlet Isolation Valve | 3 | Diaphragm Valve DN100, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC51 | _ | 061 | VCM | _ | 450S1 | Piping | C00-001 | ZC51_061VCM_450S1 | Filter Belt Supplier | Vacuum System Connection Piping | 3 | DN 450mm - OD mm - Length as per GMT drawing 7701-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 450
ZC51 | _ | 062 | VCM | _ | 450S1 | Piping | C00-001 | ZC51_062VCM_450S1 | Filter Belt Supplier | Vacuum Pump Inlet Piping | 3 | DN 450mm - OD mm - Length as per GMT drawing 7701-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 450
ZC51 | _ | 063 | VAO |  |  | Equipment | C00-001 | ZC51_063VAO | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve | 3 | Butterfly valve DN450 stainless steel, FC (Fail safe to close) with Double Acting Spring Return Actuator, flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Coated Alumninium | 450
ZC51 | _ | 063 | VAO | _ | SOV01 | Instrument | C00-001 | ZC51_063VAO_SOV01 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X
ZC51 | _ | 063 | INS | _ | ZS01 | Instrument | C00-001 | ZC51_063INS_ZS01 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Position Switch 1 | 3 | Mounted limit switch box; IP65; 2 micro switches; suitable for actuator; switching capacity 4A/250VAC-1A/24VDC SOV01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 063 | INS | _ | ZS02 | Instrument | C00-001 | ZC51_063INS_ZS02 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Position Switch 2 | 3 | Linked to ZC51_063INS_ZS01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 070 | PMP |  |  | Pump | C00-001 | ZC51_070PMP | Filter Belt Supplier | Vacuum Pump | 2 | Vacuum Pump 100-400 l/min (liquid Quanity) ~TBCm3/min (Air Quantity) @ 1 Bar Connections: flanges Inlet: DN450 Outlet: DN450 speed XXX rpm @ 50 Hz frequency range XX-50 Hz | Filter Belt Supplier | TBC | TBC | N | [54 empty] | Gardner
ZC51 | _ | 070 | PMP | _ | M01 | Motor | C00-001 | ZC51_070PMP_M01 | Filter Belt Supplier | Vacuum Pump Motor | 3 | 400V, 3Ph, 50 Hz, efficiency IE2, 1500RPM, 250 kW | Filter Belt Supplier | TBC | TBC | Y | 250 | 400 | X |  |  |  | VFD | [50 empty] | I
ZC51 | _ | 070 | PMP | _ | LS01 | Instrument | C00-001 | ZC51_070PMP_LS01 | Filter Belt Supplier | Vacuum Pump Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC R 1" Lug Connection, 316L | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X
ZC51 | _ | 070 | PMP |  |  | SKID | C00-001 | ZC51_070PMP | Filter Belt Supplier | Vacuum Pump - Skid Materials & Assembly | 2 | Vacuum Pump Stainless steel frame, as per DWG (10190-C00-DRG-GMT-XXX), as well as assembly of all internal instruments, valves and piping related to the skid. | Filter Belt Supplier | TBC | TBC | N
ZC51 | _ | 070 | PMP |  |  | SKID | C00-001 | ZC51_070PMP | Filter Belt Supplier | Vacuum Pump - Assembly Labour & Workshop Equipment | 3 | Workshop Equipment and Manpower Labour required to construct Vacuump Pump | Filter Belt Supplier | TBC | TBC | N
ZC51 | _ | 070 | PMP |  |  | SKID | C00-001 | ZC51_070PMP | Filter Belt Supplier | Vacuum Pump - Installation & Ancillary Materials | 3 | Installation items for Vacuum Pump (See 10190-C00-TDS-GMT-001), as well as Ancillary items such as insulation and wiring. | Filter Belt Supplier | TBC | TBC | N
ZC51 | _ | 071 | FIL | _ | 050S1 | Piping | C00-001 | ZC51_071FIL_050S1 | Filter Belt Supplier | Vacuum Pump Stuffing Box Drain Piping | 3 | DN 50mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
ZC51 | _ | 074 | FTR |  |  | Equipment | C00-001 | ZC51_074FTR | Filter Belt Supplier | Vacuum Pump Stuffing box | 3 |  | Filter Belt Supplier | TBC | TBC
ZC51 | _ | 077 | VAM |  |  | Valve | C00-001 | ZC51_077VAM | Filter Belt Supplier | Vacuum Pump Drain Manual Isolation Valve | 3 | Ball Valve DN50, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
ZC51 | _ | 079 | FIL | _ | 032S1 | Piping | C00-001 | ZC51_079FIL_032S1 | Filter Belt Supplier | Vacuum Pump Stuffing Box Drain Piping | 3 | DN 50mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
ZC51 | _ | 090 | CYC |  |  | Tank | C00-001 | ZC51_090CYC | Filter Belt Supplier | Vacuum Pump Outlet Separator | 3 | preliminary data consider Tank Drawing when issued D = 1 m, H= 2 m Top: 2 Flanges (1 Vacuum Outlet (DN150) + 1 Spare (DN50)) Side: 4 Flanges (1 Main Inlet (DN450), 1 Flushing Inlet (DN25), 1 air inlet (DN350), 1 flange for Level Switch Connection (DN25 with R 1" Lug Connection) + 1 side standard 800mm diameter Access Hatch Base: 2 Flanges (1 Filtrate Outlet (DN80), 1flange for Level Switch Connection (DN25 with R 1 " Lug Connection) Spare/Drain connections to be delivered with blind flanges. | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel
ZC51 | _ | 090 | CYC | _ | LS01 | Instrument | C00-001 | ZC51_090CYC_LS01 | Filter Belt Supplier | Vacuum Pump Outlet Separator High Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC R 1" Lug Connection, 316L | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 090 | CYC | _ | LS02 | Instrument | C00-001 | ZC51_090CYC_LS02 | Filter Belt Supplier | Vacuum Pump Outlet Separator Low Switch | 3 | Vibratory probe, side mounted, 3-wire PNP 24VDC R 1" Lug Connection, 316L | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 091 | VCM | _ | 150S1 | Piping | C00-001 | ZC51_091VCM_150S1 | Filter Belt Supplier | Vacuum System Gas Outlet Piping | 3 | DN 150mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150
ZC51 | _ | 092 | PRW | _ | 065S1 | Piping | C00-001 | ZC51_092PRW_065S1 | Filter Belt Supplier | Vacuum System Water Inlet Piping | 3 | DN 65mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65
ZC51 | _ | 093 | VAO |  |  | Equipment | C00-001 | ZC51_093VAO | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve | 3 | Ball Valve DN65 stainless steel, FC (Fail safe to close) with Single Acting Spring Return Actuator, flanged | Filter Belt Supplier | TBC | TBC | N | [9 empty] | C | [10 empty] | Coated Alumninium | 65
ZC51 | _ | 093 | VAO | _ | SOV01 | Instrument | C00-001 | ZC51_093VAO_SOV01 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Solenoid | 3 | Solenoid pilot valve 3/2-ways, 24VDC | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 093 | INS | _ | ZS01 | Instrument | C00-001 | ZC51_093INS_ZS01 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Position Switch 1 | 3 | Mounted limit switch box; IP65; 2 micro switches; suitable for actuator; switching capacity 4A/250VAC-1A/24VDC SOV01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 093 | INS | _ | ZS02 | Instrument | C00-001 | ZC51_093INS_ZS02 | Filter Belt Supplier | Vacuum Pump Bypass Actuated Valve Position Switch 2 | 3 | Linked to ZC51_093INS_ZS01 | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X | [53 empty] | I
ZC51 | _ | 095 | FIL | _ | 065S1 | Piping | C00-001 | ZC51_095FIL_065S1 | Filter Belt Supplier | Vacuum System Bypass Piping | 3 | DN 65mm - OD mm - Length as per GMT drawing 7701-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65
ZC51 | _ | 107 | VAM |  |  | Valve | C00-001 | ZC51_107VAM | Filter Belt Supplier | Vacuum System Outlet Manual Isolation Valve | 3 | Butterfly Valve DN65, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 65
ZC51 | _ | 115 | FIL | _ | 100S1 | Piping | C00-001 | ZC51_115FIL_100S1 | Filter Belt Supplier | Vacuum Pump Outlet Separator Piping | 3 | DN 50mm - OD mm - Length as per GMT drawing 7701-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
ZC51 | _ | 118 | VAM |  |  | Valve | C00-001 | ZC51_118VAM | Filter Belt Supplier | Vacuum System Exchanger Outlet Manual Isolation Valve | 3 | Butterfly Valve DN100, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC51 | _ | 120 | EXC |  |  | Equipment | C00-001 | ZC51_120EXC | Filter Belt Supplier | Vacuum Pump Cooling Heat Exchanger | 3 | Shell & Tube Heat Exchanger. Surface Area- TBC Heat Load- TBC Duty Range- 13000 kg/hr (@ 3 bar) Connections- Vacuum Pump Inlet (DN100 Flanged), Vacuum Pump Outlet (DN100 Flanged), Cooling Water Connections (DN80 Flanged) | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100 | [6 empty] | Glycol
ZC51 | _ | 120 | INS | _ | FT01 | Instrument | C00-001 | ZC51_120INS_FT01 | Filter Belt Supplier | Vacuum Pump Cooling Flow Transmitter | 3 | Variable Area type, 0.75 - 5 m3/h @ 6 barg - 10°C -1000 kg/m3, DN04 (5/32") (wafer connection DN25 = 1"), in-line vertical mounting, accuracy 0.2%, 4-20mA Hart, 24VDC (note: no grounding rings required for SS pipes) | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | 4..20mA | [46 empty] | BHS |  |  | I
ZC51 | _ | 120 | INS | _ | TT01 | Instrument | C00-001 | ZC51_120INS_TT01 | Filter Belt Supplier | Vacuum Pump Cooling Temperature Transmitter | 3 | Inline Mounted RTD Thermometer 0 - 100°C Type: PT100 with Thermowell Insertion 100 mm Control: Profibus PA transmitter, 24VDC Process Connection: DN25 (R 1") Threaded | Filter Belt Supplier | TBC | TBC | Y |  | 24 |  | X |  |  |  | 4..20mA | [46 empty] | E&H |  |  | I
ZC51 | _ | 123 | VAM |  |  | Valve | C00-001 | ZC51_123VAM | Filter Belt Supplier | Vacuum System Exchanger Inlet Manual Isolation Valve | 3 | Butterfly Valve DN100, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 100
ZC51 | _ | 127 | VAM |  |  | Valve | C00-001 | ZC51_127VAM | Filter Belt Supplier | Vacuum System Exchanger Inlet Drain Valve | 3 | Ball Valve DN25, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 25
ZC51 | _ | 137 | VAM |  |  | Valve | C00-001 | ZC51_137VAM | Filter Belt Supplier | Chiller Piping Inlet Drain Valve | 3 | Ball Valve DN50, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
ZC51 | _ | 138 | VAM |  |  | Valve | C00-001 | ZC51_138VAM | Filter Belt Supplier | Heat Exchanger Cooling Outlet Manual Isolation Valve | 3 | Butterfly Valve DN150, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150
ZC51 | _ | 139 | GCL | _ | 150S1 | Piping | C00-001 | ZC51_139GCL_150S1 | Filter Belt Supplier | Heat Exchanger Cooling Outlet Piping | 3 | DN 150mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150
ZC51 | _ | 140 | EXC |  |  | Equipment | C00-001 | ZC51_140EXC | Chiller | Vacuum System Chiller | 3 | Self contained Chilling System, to be provided with all valves, electrical and control systems included in a single package. | Chiller | TBC | TBC | Y | 127.7 | 400
ZC51 | _ | 142 | GCL | _ | 150S1 | Piping | C00-001 | ZC51_142GCL_150S1 | Filter Belt Supplier | Heat Exchanger Cooling Inlet Piping | 3 | DN 150mm - OD mm - Length as per GMT drawing 10190-C51-DMF-GMT-XXX | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 150
ZC51 | _ | 143 | VAM |  |  | Equipment | C00-001 | ZC51_143VAM | Filter Belt Supplier | Vacuum Pump Bypass Manual Valve | 3 | Ball Valve DN150 stainless steel | Filter Belt Supplier | TBC | TBC | N | [9 empty] | C | [10 empty] | Coated Alumninium | 150 | [35 empty] | H
ZC51 | _ | 147 | VAM |  |  | Valve | C00-001 | ZC51_147VAM | Filter Belt Supplier | Chiller Piping Inlet Drain Valve | 3 | Ball Valve DN50, Flanged | Filter Belt Supplier | TBC | TBC | N | [20 empty] | Stainless Steel | 50
[10 empty] | UPS | 3 | Uninterruptable Power Supply |  |  |  | N | 50 | 380
463.2
Added item (Confirmed)
Added Item (Provisional)
Deleted item
Note
[8 empty] | REV |  | DATE | [6 empty] | DESCRIPTION | [53 empty] | BY |  | APPROVED
[8 empty] | A |  | 2024-07-24 |  | First Issue for Tender (Indicative List only)
Saint-Gobain – Gypsum Manufacturing Technology, East Leake, Loughborough, LE12 6JS U.K. Tel: 0115 945 1600

## Instructions
Best practice is to use columns A-F to create the SG tag, rather than entering directly. This allows faster filtering.
If you have just whole tags to work with, they can be divided into sections. See the 'Tag_splitter' worksheet in this workbook.
Use the revision column to enter a revision letter for any line that has changed, and a/d/r letter in the adjacent column to show the type of change (conditional formatting is applied based on this).
Try to avoid blank rows in the list - filtering and searchability is better without gaps
To reduce un-necessary data, where a column could have a Yes/No type answer, simply place an 'x' to indicate 'Yes'
P&ID can be shown as short form. For example E10-001 = xxxx-E10-DEL-GMT-001 where xxxx is project number
Not all columns need to be filled.
In the early stages of design, if no specific model needs to be specified use can be made of other columns to show required functionality etc

## Tag_splitter
To divide S-G tags into their constituent parts:
1. Copy the list of tags you want to convert.
2. Use the 'paste special' command for 'values' to add them in column B, from row 9 down
3. Copy the formula in cells C4:H4 and paste beside the list of plain text tags you need to split
| Plain text tag | Line-Process area number | Separator [ _ ] | Equipment number | Equipment Descriptor | Separator [ _ ] | Sub-comp. items number
Example | AE10_050INS_FT1 | AE10 | _ | 050 | INS | _ | FT1

## Pick_lists
Design Status
Pre engineering information
Prelim detailed design
Information as order placed
Confirmed as construction by supplier
Motor Control Method
DOL
DOL reversing
VFD
Soft-start
Soft-start reversing
Servo (no brake)
Servo (brake)
Signal Type to PLC
4..20mA
Discrete
Ethernet/IP
Modbus RTU
Modbus TCP
Profibus DP
Profibus PA
Profinet
Sensor Technology
Optical
Inductive
Pressure
Weighing
Capacitive
Microwave
Ultrasonic
Description | Example | Class
Actuated Valve | VAA | C12
Ball Mill | MIL | C04
Belt Conveyor | COB | C01
Belt tension station |  | C31
Belt tracking station |  | C32
Belt wash station |  | C30
Big Bag Unloader | BBU | C09
Blower (cutter) |  | C36
Board alignment |  | C49
Board encoder (cutter) | CUT | C35
Board inverter (booker) | INV | C38
Board spraying unit | BSP | C33
Bundler | SAW | C46
Burner | BNR | C56
Burner skid |  | C57
Cascade |  | C44
Corner transfer |  | C45
Creaser | CRS | C24
Culls cutter |  | C53
Cutter | CUT | C34
Dense Phase |  | C54
Dryer |  | C42
Dryer infeed |  | C41
Dryer outfeed |  | C43
Dust Collector | DCL | C10
Elevators | ELV | C07
Extruder | EXT | C22
Fan | FAN | C55
Filter System | FTR | C17
Flexible Coupling | FLX | C11
Flow Switch/Level Switch/Temperature Sensor | FS/LS/TE | C19
Flow/Level Transmitter | FT | C15
Foam Generator | FMG | C18
Forming conveyor | COB | C27
Heat Exchanger | HEX | C59
Ironing bar | BSB | C29
Lifting teble (table A) | LFT | C37
Loss in Weigth feeder | LIW | C06
Manual valves (dampers?) | VAM | C58
Mini-stacker |  | C47
Mixer | MIX | C20
Moisture sensor (Dryer and Take-off) | MT | C60
Other rotating machines | AAA | C03
Palet conveyor |  | C50
Paper Stand | PUS | C25
Pumps | PMP | C16
Roller coater | RC | C23
Roller conveyor | COR | C51
Screw Conveyor | COS | C02
Silos and Bins | SIL | C08
Solenoid Valve/Manual Valve with Limit Switches | VAO | C14
Splicer | SPL | C26
Stack inverter | INV | C52
Stacking table |  | C48
Stucco Cooler | SCL | C13
Temperature Transmitter (Dryer and Take-off) | TT | C61
Tipple | LFT | C40
Vibrating Table | VIB | C21
Walker wheel | BWB | C28
Weighbelt feeder | WBF | C05
Weighing system | WEH | C39